| !MM-5 Verification setpoint file |  |  |  |
| --- | --- | --- | --- |
| !Version | P | 2/17/2002 | RHW |
| !Address | SP Val | Name | Description |
| 0x00 | 5003 | C_MAGIC | Magic Number |
| 0x01 | 5825 | CAL_VOUTSET | Cal Vout AC - relates Vnominal AC (VM) to required AMPDAC value |
| 0x02 | 0 | P_PERTURB | Amount export power is perturbed (1/sec) - PP10 only |
| 0x03 | 30 | MAX_MISSED_ZC | Max missed Zcs to stop export |
| 0x04 | 4 | AIV_GAIN | Anti-islanding gain - voltage/power shift |
| 0x05 | 4 | AIF_GAIN | Anti-islanding gain - phase/frequency shift |
| 0x11 | 30 | MIN_TRANSITION_TIME | Transition Delay |
| 0x12 | 590 | VBAT_MAX | VbatMax - non-temp comp batt charge limit |
| 0x13 | 4 | spSP_ISLAND_LOG_LEVEL | Island accel level (V or F) must be greater than this value for logging to occur |
| 0x14 | 116 | spSP_VERSION | 100*N+letter of alphabet - Update this with each rev of setpoint file |
| 0x15 | 0 | spCOMM_TIMEOUT | If non-zero, will shutdown inverter in this many seconds |
| 0x16 | 60 | spRETRY_COUNT_RESET_TIME | The retry counter is zeroed if the inverter runs OK for this number of seconds |
| 0x17 | 30 | spZERO_CURRENT_HOLD_TIME | Time after sun-up and achieving float to hold, before going to zero current mode |
| 0x18 | 30 | MPPT IV Scan Period | Time between periodic IV scans |
| 0x19 | 1 | MPPT_FILTER_OFFSET | MPPT Filter offset. + makes filter tend down in voltage. (unsigned) |
| 0x1A | 2 | MPPT_FILTER_LENGTH | Length of moving average filter for MPPT direction determination |
| 0x1B | 15 | MPPT_MAX_WALK | Maximum steps in any direction before changing direction and resetting filter |
| 0x1C | 2 | MPPT_STEP | Voltage step size in V/10 for MPPT tracking |
| 0x1D | 2000 | IBAT_LIMIT | Ibat Max Discharge Amps x 10 |
| 0x1E | 900 | IIN_FAST_LIM | fast dc-dc backoff on Iin & Ibat |
| 0x1F | 120 | CLIP_RUN | Hardware Clip current Limit for Run |
| 0x20 | 420 | VBAT_LOW | Low Battery Shutdown |
| 0x21 | 620 | VBAT_HIGH | High battery shutdown |
| 0x22 | 1200 | VM_VAC | VM Nominal AC Output Voltage (V) |
| 0x23 | 600 | VM_FREQ | VM SA Frequency (Hz x 10) |
| 0x24 | 5000 | NOM_INV_POWER | Nom Inverter Power |
| 0x26 | 0 | VM_DROOP | VM Droop (V/Amp x ???) |
| 0x27 | 255 | VM_GC_DROOP | CM Droop (for transitions) |
| 0x28 | 1080 | GC_VMIN | CM Vout Min (V) |
| 0x29 | 1320 | GC_VMAX | CM Vout Max (V) |
| 0x2A | 125 | GC_VQMIN | CM Quick Vmin trip (raw A/D Counts) |
| 0x2B | 210 | GC_VQMAX | CM Quick Vmax trip (raw A/D Counts) |
| 0x2C | 5940 | GC_FMIN | CM Freq min (Hz x 10) |
| 0x2D | 6030 | GC_FMAX | CM Freq max (Hz x 10) |
| 0x2E | 5 | GC_SHORT_WTIME | CM Short wait time till restart (non grid fail) |
| 0x2F | 300 | GC_LONG_WTIME | CM Long wait time till restart after grid fail. Set to 300 after testing |
| 0x30 | 0 | VIN_LOW | VIN_LOW - Min PV input voltage |
| 0x31 | 1200 | VIN_HIGH | VIN_HIGH - Max PV Input voltage |
| 0x32 | 1000 | IIN_MAX | IIN_MAX - Iin Max - Max PV Input Current |
| 0x33 | 50 | MPPT_SCAN_RANGE | +/- excursion from current PWM, in PWM units |
| 0x34 | 500 | VIN_MPPL | VIN_MPPL - Not used PP |
| 0x35 | 850 | VIN_MPPH | VIN_MPPH - Not used PP |
| 0x36 | 650 | VIN_NOM | Active Vin limit |
| 0x37 | 1000 | IBAT_CHG_MAX | IBAT_CHG_MAX - Max Batt Chg Current (Initial val and upper limit of chg current command) |
| 0x38 | 105 | GEN_VMIN | GEN_VMIN - Not used PP |
| 0x39 | 132 | GEN_VMAX | GEN_VMAX - Not used PP |
| 0x3A | 580 | GEN_FMIN | GEN_FMIN - Not used PP |
| 0x3B | 620 | GEN_FMAX | GEN_FMAX - Not used PP |
| 0x3C | 10 | GEN_ICHGMAX | GEN_ICHGMAX - Not used PP |
| 0x3D | 0 | GEN_DROOP | GEN_DROOP - Not used PP |
| 0x3E | 5 | RIPPLE_SHIFT | RIPPLE_SHIFT - Phase of ripple compensation to be removed) |
| 0x3F | 140 | RIPPLE_COMP | RIPPLE_COMP - amount of pwm change per batt ripple unit |
| 0x40 | 1 | BATTERY_TYPE | BATTERY_TYPE - not used at present |
| 0x41 | 0 | PBAT_CHG_MAX | PBAT_CHG_MAX - Max Batt Charge AC Power input - not used at present |
| 0x42 | 545 | VBAT_FLOAT | VBAT_FLOAT |
| 0x43 | 15 | TIME_FLOAT | TIME_FLOAT |
| 0x44 | 565 | VBAT_BULK | VBAT_BULK |
| 0x45 | 60 | TIME_BULK | TIME_BULK |
| 0x46 | 460 | BULK_TRIG_V | BULK_TRIG_V |
| 0x47 | 300 | BULK_TRIG_CHG | BULK_TRIG_CHG |
| 0x48 | 565 | VBAT_BOOST | VBAT_BOOST |
| 0x49 | 180 | TIME_BOOST | TIME_BOOST |
| 0x4A | 30 | BOOST_INTERVAL | BOOST_INTERVAL |
| 0x4C | 170 | VBAT_TEMP_MAX | VBAT_TEMP_MAX - Shutdown Temperature - degC+100-not used |
| 0x4E | 25 | TEMPCO_L | TEMPCO_L - (0.01%/degC) - below 25C |
| 0x4F | 15 | TEMPCO_H | TEMPCO_H - (0.01%/degC) - above 25C |
| 0x50 | 800 | BB_CAPACITY | BB_CAPACITY - Batt Capacity (AH x 10) |
| 0x51 | 80 | BB_EFF_BREAK | BB_EFF_BREAK - % capacity for efficiency change |
| 0x52 | 98 | BB_EFF_LOW | BB_EFF_LOW |
| 0x53 | 90 | BB_EFF_HIGH | BB_EFF_HIGH - % efficiency above break |
| 0x54 | 0 | BB_ZEROCURRENT | BB_ZEROCURRENT - ??? |
| 0x55 | 430 | BB_VOLTAGE_0 | BB_VOLTAGE_0 |
| 0x56 | 470 | BB_VOLTAGE_50 | BB_VOLTAGE_50 |
| 0x57 | 510 | BB_VOLTAGE_80 | BB_VOLTAGE_80 |
| 0x60 | 101 | MECHANICAL_REVISION |  |
| 0x68 | 180 | Access timeout=3 minutes; > 200 means no timeout |  |
| 0x6e | 0 | BAUD RATE; 0=19.2K, 1=9600; 2=4800 maybe |  |
| 0x6F | 65535 | COMM_ADDRESS |  |
| 0x70 | 140 | FAN_TEMP | FAN_TEMP |
| 0x71 | 16 | FAN_GAIN | FAN_GAIN |
| 0x72 | 175 | TEMP_WARN | TEMP_WARN |
| 0x73 | 185 | TEMP_SHUTDOWN | TEMP_SHUTDOWN |
| 0x74 | 100 | HYST_NORM | HYST_NORM |
| 0x75 | 55 | HYST_MULT | HYST_MULT |
| 0x76 | 16 | HYST_LIM_LO | HYST_LIM_LO |
| 0x77 | 192 | HYST_LIM_HI | HYST_LIM_HI |
| 0x78 | 500 | I2T_DC_INPUT | I2T limit for battery breaker |
| 0x79 | 136 | VM_OFFSET | VM_OFFSET - used internally in the inverter to store dc offset to transformer |
| 0x7A | 4 | PHASE_BIAS | PHASE_BIAS |
| 0x7B | 100 | IPRI_CLIP_LIMIT | IPRI_CLIP_LIMIT |
| 0x7F | 22 | SYS_OPTION | SYS_OPTION=0x10=16=no mppt (test), exsby=18(+MPPT) for ship |
| 0x80 | 1000 | PP_INITIAL_IIN | PP_INITIAL_IIN - Initial DCL |
| 0x81 | 50 | PP_INITIAL_PEX | PP_INITIAL_PEX - Initial Power Request |
| 0x82 | 2 | PP_PRIMARY_MODE | PP_PRIMARY_MODE |
| 0x83 | 3 | PP_SECONDARY_MODE | PP_SECONDARY_MODE |
| 0x85 | 0 | DEFAULT_MANUAL_MODE | DEFAULT_MANUAL_MODE |
| 0x86 | 1 | SET_AUTO_MODE | SET_AUTO_MODE |
| 0x87 | 5 | SA_OVERLOAD_MAX_SECONDS | SA_OVERLOAD_MAX_SECONDS |
| 0x88 | 5 | SA_OVERLOAD_RETRIES | SA_OVERLOAD_RETRIES |
| 0x89 | 10 | SA_OVERLOAD_RETRY_DELAY | Seconds |
| 0x8A | 0 | GC_LINE_RESISTANCE | GC mode Line resistance m Ohm compensation for voltage |