## Sheet1
Name	Envoy Type	Min Envoy Version	Reference voltage	Nominal frequency	Over voltage trip time	Over voltage limit	Over voltage trip time 2	Over voltage limit 2	Over voltage trip time (slow)	Over voltage limit (slow)	Average over voltage	Over voltage momentary cessation start voltage	Under voltage trip time	Under voltage limit	Under voltage trip time 2	Under voltage limit 2	Under voltage trip time (slow)	Under voltage limit (slow)	Under voltage momentary cessation start voltage	Reconnect AC voltage high	Reconnect AC voltage low	Over frequency trip time	Over frequency limit	Over frequency trip time (slow)	Over frequency limit (slow)	Under frequency trip time	Under frequency limit	Under frequency trip time (slow)	Under frequency limit (slow)	Reconnect AC frequency high	Reconnect AC frequency low	Frequency variation trip time	Frequency variation limit	Vector shift trip time	Vector shift trip limit	Start / Reconnect time	Anti-islanding reconnect time (short)	Anti-islanding reconnect time (long)	Apply limits after voltage trip	Apply limits after frequency trip	Apply limits after anti-islanding trip	Apply limits after rate of change of frequency trip	Apply limits after vector shift trip	External AC disconnect relay enabled	Reconnect delay	Normal ramp rate	Soft-start ramp rate	DC current injection mode	Islanding detection enabled	Anti-islanding threshold trip time	Over voltage power limit enabled	Over voltage power limit start voltage	Over voltage power limit start power	Over voltage power limit end voltage	Over voltage power limit minimum power	Under voltage charge limit enabled	Under voltage charge limit start voltage	Under voltage charge limit start power	Under voltage charge limit end voltage	Under voltage charge limit minimum power	Over frequency power limit enabled	Start frequency	Start delay	Ramp down rate	Hysteresis	Ramp up frequency (max)	Ramp up frequency (min)	Ramp up delay time	Ramp up rate	Ramp up rate (low)	Under frequency charge limit enabled	Start frequency	Start delay	Ramp down rate	Hysteresis	Ramp up frequency (min)	Ramp up frequency (max)	Ramp up delay time	Ramp up rate	Ramp up rate (low)	Fixed power factor enabled	Fixed power factor	Watt power factor enabled	Start power
AC Coupling FW83pct/Hz PEL100W REC300s	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	62	10,000	61.5	10,000	57.5	300,000	59.2	61.2	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		83	No	61.1	58.6	0			No				No						No	1	No	50
AC Coupling PE test 83/Hz	North America	4.4	120	60	160	144			1,000	132		132	160	60			2,000	105.6	54	132	105.6	160	62			160	59.3			62	59.3		0			60	300	60	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		83	No	61.1	58.6	0			No				No						No	1	No	50
CA Rule21 201709	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127	106	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	No	120	100	129.6	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201709 ,10kW PEL	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127	106	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	No	120	100	129.6	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201709 w/ VW	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127	106	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201807 VV RPP VW 15 kW PEL	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201807 VV RPP VW 17.1 kW PEL	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201807 VV w/ RPP	North America	4.1	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127	106	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	No	121	100	132	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201807 VV w/ RPP VW	North America	4.1	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127	106	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			No	60.2		100	No	60.1	59.5		50	50	No				No						No	1	No
CA Rule21 201902 NPR VV VW FW	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	94.8	94.8	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CA Rule21 201902 VV VW FW	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CA Rule21 201902 VV VW FW PEL6KW WHB	North America	6	120	60	160	144			13,000	132		132	50	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CA Rule21 201902 VV VW FW PEL6kW	North America	4.4	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CA Rule21 201902 VV VW FW WHB	North America	6	120	60	160	144			13,000	132		132	50	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CA Rule21 201902 VV VW FW, No Export	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
CO LPEA 201906 VV, VW, FW	North America	4.5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	132	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	305	305	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	126	100	128.4	0	No		100			Yes	60.1	0	50	No		59.9			50	No	59.9		50	No						No	0.95	No
IEEE 1547 2015 Orange Rockland	North America	4.4	120	60	160	144			2,000	132	144		160	54			2,000	84		127.2	105.6	160	62	300,000	61.2	160	56.5	300,000	58.5	60.5	59.3	10,000	5	0	0	305	305	305	Yes	Yes	Yes	No	No	No	10,000		0	None	Yes	80	No	131	100	132	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
IEEE 1547:2015 - PECO WHB	North America	6	120	60	160	144			60,000	126.5			50	60			2,000	105.6		126	105.6	160	62	2,000	60.5	160	57	2,000	59.5	60.5	59.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	10	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.04	0	33.33	No	61.1	58.9	0	0.333	0.333	No	59.96	0	33.33	No	61.1	58.9	0	0.333	0.333	No	1	No	50
IEEE 1547:2015 19.2 kW PEL	North America	5	120	60	160	144			1,000	132			160	54	1,000	72	2,000	105.6		132	105.6	160	62	2,000	60.5	160	57	2,000	59.5	60.5	59.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	10	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.04	0	33.33	No	61.1	58.9	0	0.333	0.333	No	59.96	0	33.33	No	61.1	58.9	0	0.333	0.333	No	1	No
IEEE 1547:2015 38.4 kW PEL	North America	5	120	60	160	144			1,000	132			160	54	1,000	72	2,000	105.6		132	105.6	160	62	2,000	60.5	160	57	2,000	59.5	60.5	59.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	10	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.04	0	33.33	No	61.1	58.9	0	0.333	0.333	No	59.96	0	33.33	No	61.1	58.9	0	0.333	0.333	No	1	No
IEEE 1547:2015 Ameren	North America	5	120	60	160	144			13,000	132		132	1,500	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	2	None	Yes	80	No	127.2	100	132	0	No		100			No	60.04		50	No	60.1	59.5		50	50	No	59.96		50	No	60.1	59.9		50	50	No	0.95	No
IEEE 1547:2015-WHB	North America	6	120	60	160	144			1,000	132			50	60			2,000	105.6		132	105.6	160	62	2,000	60.5	160	57	2,000	59.5	60.5	59.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	10	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.04	0	33.33	No	61.1	58.9	0	0.333	0.333	No	59.96	0	33.33	No	61.1	58.9	0	0.333	0.333	No	1	No	50
ISO-NE 2018	North America	4.4	120	60	160	144			2,000	132	0	145	1,100	60			2,000	105.6		132	105.6	160	62	300,000	61.2	160	56.5	300,000	58.5	61.2	58.5		0	0	0	300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	2	None	Yes	2,000	No	131	100	132	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
ISO-NE 2018 WHB	North America	6	120	60	160	144			2,000	132	0	145	50	60			2,000	105.6		132	105.6	160	62	300,000	61.2	160	56.5	300,000	58.5	61.2	58.5		0	0	0	300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	2	None	Yes	2,000	No	131	100	132	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
Louisiana-IQ PW2	North America	4.4	120	60	160	144			1,000	132		132	160	60			2,000	105.6	60	132	105.6	160	62			160	59.3			61.5	59.3	10,000	5			10	300	10	Yes	Yes	Yes	No	No	Yes	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2	0	83	No	60.1	59.9	0	50	50	No	59.96	0	33.33	No	60.1	59.9	0	50	50	No	1	No	50
Off-Grid FW83	North America	4.4	127	60	160	144			1,000	141	144		160	60			2,000	102		139.7	103	160	62	1,000	61.5	160	50			61.5	58	1,000	5	0	0	5	5	5	Yes	Yes	Yes	No	No	No	10,000		0	None	No	2,000	No	131	100	132	99.7	No	120	100	114	0	Yes	60.2	0	83.33	No	60.1	56	15	4	2	No	59.75		133.33	No	59.85	60.25	60	0.278	0.278	No	0.9	No	50
PREPA 2017 FW100	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	61.5	2,000	61.2	10,000	57.5	300,000	59.2	61.1	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.1		100	No	61.1	58.6	0			No				No						No	0.98	No	50
PREPA 2017 FW100 No Export	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	61.5	2,000	61.2	10,000	57.5	300,000	59.2	61.1	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.1		100	No	61.1	58.6	0			No				No						No	0.98	No	50
PREPA 2017 FW100 PF98	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	61.5	2,000	61.2	10,000	57.5	300,000	59.2	61.1	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.1		100	No	61.1	58.6	0			No				No						Yes	0.98	No	50
PREPA 2017 FW55	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	62			10,000	57.5	300,000	59.2	62	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		55	No	61.1	58.6	0			No				No						No	0.98	No	50
PREPA 2017 FW55 No Export	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	62			10,000	57.5	300,000	59.2	62	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		55	No	61.1	58.6	0			No				No						No	0.98	No	50
PREPA 2017 FW60	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	62	2,000	61.9	10,000	57.5	300,000	59.2	61.4	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		60	No	61.1	58.6	0			No				No						No	1	No	50
PREPA 2017 FW60 PF98	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	160	62	10,000	61.8	10,000	57.5	300,000	59.2	61.4	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		60	No	61.1	58.6	0			No				No						Yes	0.98	No	50
PREPA 2017 FW83	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	10,000	61.5	300,000	61.41	10,000	57.5	300,000	59.2	61.4	59.2		0			300	300	300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2		83	No	61.1	58.6	0			No				No						No	1	No	50
PREPA 2017 FW83 AV	North America	4.4	120	60	160	144			1,000	138		138	160	54	1,000	72	2,000	105.6	54	138	105.6	10,000	61.5	300,000	61.41	10,000	57.5	300,000	59.2	61.4	59.2	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2	0	83	No	61.1	58.6	0	0.333	0.333	No				No						No	1	No	50
PREPA 2017 S/IQ VV VW FW83	North America	4.4	120	60	160	144			1,000	132		132	160	54	1,000	72	2,000	105.6	54	132	105.6	10,000	61.5	300,000	61.4	10,000	57.5	300,000	59.2	60.5	59.2		0			305	300	60	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	Yes	130.8	100	132	0	No		100			Yes	60.2		83	No	61.1	58.6	0			No				No						No	1	No	50
PREPA 2017 SERIE M	North America	4.4	120	60	160	144			1,000	132	132		160	54			1,000	105.6		132	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					305	60	305	Yes	Yes	Yes	No	No	Yes	10,000		0	None	Yes	2,000	No	123.8	100	124.7	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
PREPA 2017 SERIE M AV	North America	4.4	120	60	160	144			1,000	138	138		160	54			1,000	105.6		138	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					305	60	305	Yes	Yes	Yes	No	No	Yes	10,000		0	None	Yes	2,000	No	123.8	100	124.7	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
PREPA 2017 SERIE M FW100	North America	4.4	120	60	160	144			1,000	132		132	160	54			2,000	105.6	54	132	105.6	160	61.5	2,000	61.2	10,000	57.5	300,000	59.2	61.1	59.2	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.1	0	100	No	61.1	58.6	0	0.333	0.333	No				No						No	1	No	50
PREPA 2017 SERIE M FW83	North America	4.4	120	60	160	144			1,000	132		132	160	54			2,000	105.6	54	132	105.6	10,000	61.5	300,000	61.41	10,000	57.5	300,000	59.2	61.4	59.2	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			Yes	60.2	0	83	No	61.1	58.6	0	0.333	0.333	No				No						No	1	No	50
PREPA 2017 SERIE S/IQ	North America	4.4	120	60	160	144			1,000	132	132		160	54	1,000	72	2,000	105.6		132	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					305	60	305	Yes	Yes	Yes	No	No	Yes	10,000		0	None	Yes	2,000	No	123.8	100	124.7	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
PREPA 2017 SERIE S/IQ AGF	North America	4.4	120	60	160	144			1,000	138	138	145	160	60	1,000	72	2,000	105.6	60	138	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					300		300	Yes	Yes	Yes	No	No	No	10,000	100	0.33	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.2	0	33.33	No	60.1	56				No				No						No	0.95	No	50
PREPA 2017 SERIE S/IQ AV	North America	4.4	120	60	160	144			1,000	138	138		160	54	1,000	72	2,000	105.6		138	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					305	60	305	Yes	Yes	Yes	No	No	Yes	10,000		0	None	Yes	2,000	No	123.8	100	124.7	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
PREPA 2017 SERIE S/IQ AV 5sREC	North America	4.4	120	60	160	144			1,000	138	138		160	54	1,000	72	2,000	105.6		138	105.6	10,000	61.5	300,000	60.5	10,000	57.5	300,000	59.2	60.5	59.2					5	60	305	Yes	Yes	Yes	No	No	Yes	10,000		0	None	Yes	2,000	No	123.8	100	124.7	99.7	No		100			No	62	0	83.33	No	60.5	56	300	4	2	No				No						No		No
TEST ENS CA Rule21 201902 VV VW FW 50ms 60V	North America	6	120	60	160	144			13,000	132		132	50	60	11,000	84	21,000	105.6	60	127.2	105.6	160	62	300,000	60.5	160	57	300,000	58.5	60.5	58.5					15	15	15	Yes	Yes	Yes	No	No	No	10,000	100	2	None	Yes	80	Yes	127.2	100	132	0	No		100			Yes	60.04		50	No	60.1	59.5		50	50	Yes	59.96		50	No						No	0.95	No
TEST IEEE 1547:2015 50 ms 60 V	North America	6	120	60	160	144			1,000	132		132	50	60			2,000	105.6	60	132	105.6	160	62	2,000	60.5	160	57	2,000	59.5	60.5	59.5	10,000	5			300	300	300	Yes	Yes	Yes	No	No	Yes	10,000	100	10	None	Yes	2,000	No	127.2	100	132	0	No		100			No	60.04	0	33.33	No	61.1	58.9	0	0.333	0.333	No	59.96	0	33.33	No	61.1	58.9	0	0.333	0.333	No	1	No	50