## Read Me
Pika Energy Island System Sizing
Use this spreadsheet when planning to install a solar array and/or smart batteries with the Pika Energy Island.
Use the 'PV Link Sizing' tab to determine the number of any given solar panel that can be connected in series into a PV Link MPPT device.
Use the 'Dedicated Loads Layout' tab when deciding which loads to back up with one or more of Pika's smart battery options.
For more Pika installer resources, visit:
https://www.pika-energy.com/installer-resources/

## Dedicated Loads Layout
[8 empty] | Use this sheet when sizing one or more Pika Smart Batteries to provide backup power during outage events. Use the table to add loads, specifying the quantity, power, and duration requirements. The power specs of loads listed here are for general purposes. Check the specifications of the actual loads to be backed up. | Usable Energy | # Batteries
Sizing Dedicated Loads Panel for Backup Power | [7 empty] | Enter inputs in yellow cells only |  | 1 | 2 | 3 | 4
[8 empty] | Outputs appear in green cells | Harbor Plus | 17.1 | 34.2 | 51.3 | 68.4
Smart Battery Type | Harbor Plus | [7 empty] | Harbor Flex | 11.4 | 22.8 | 34.2 | 45.6
# of Smart Batteries | 1 | [7 empty] | Coral Smart Battery | 14 | 28 | 42 | 56
Max # of PV Links (for PV array) | 9 | [7 empty] | Continuous Power | # Batteries
[10 empty] | 1 | 2 | 3 | 4
| Units | Smart Battery Specs | Dedicated Loads System Requirements | Difference |  |  |  |  | Harbor Plus | 6.7 | 8 | 8 | 8
Max. Surge Power (up to 5 minutes) | W | 10000 | 0 | 10000 |  |  |  |  | Harbor Flex | 4.5 | 8 | 8 | 8
Max. Continuous Power | W | 6700 | 0 | 6700 |  |  |  |  | Coral Smart Battery | 8 | 8 | 8 | 8
Usable Energy Capacity | Wh | 17100 | 0 | 17100
[9 empty] | Surge Power | # Batteries
Loads | Quantity | Surge Load (W) | Total Surge Load (W) | Continuous Load (W) | Total Continuous Load (W) | Duration (Hours) | Total Energy Required (Wh) |  |  | 1 | 2 | 3 | 4
Air Conditioner |  | 300 | 0 | 300 | 0 |  | 0 |  | Harbor Plus | 10 | 12 | 12 | 12
Boiler |  | 100 | 0 | 100 | 0 |  | 0 |  | Harbor Flex | 7 | 12 | 12 | 12
CFL Lightbulbs |  | 15 | 0 | 15 | 0 |  | 0 |  | Coral Smart Battery | 12 | 12 | 12 | 12
Chest Freezer |  | 200 | 0 | 200 | 0 |  | 0
Circulator Pumps |  | 600 | 0 | 150 | 0 |  | 0 |  | PV to Smart Battery Ratio | # Batteries
Electric Dryer |  | 3000 | 0 | 3000 | 0 |  | 0
Furnace Fan |  | 600 | 0 | 600 | 0 |  | 0 |  | # Batteries | 0 | 1 | 2 | 3 | 4
Heat Pump |  | 300 | 0 | 300 | 0 |  | 0 |  | Max PV Links | 12 | 9 | 6 | 3 | 0
LED Lightbulbs |  | 8 | 0 | 8 | 0 |  | 0
Microwave |  | 900 | 0 | 900 | 0 |  | 0
Oven |  | 2400 | 0 | 2400 | 0 |  | 0
Refrigerator |  | 200 | 0 | 200 | 0 |  | 0
Resistive Heater |  | 1000 | 0 | 1000 | 0 |  | 0
Small Appliances |  | 300 | 0 | 100 | 0 |  | 0
Stove |  | 1500 | 0 | 1500 | 0 |  | 0
Sump Pump |  | 1400 | 0 | 350 | 0 |  | 0
TV |  | 300 | 0 | 300 | 0 |  | 0
Washing Machine |  | 800 | 0 | 800 | 0 |  | 0
Water Heater |  | 350 | 0 | 350 | 0 |  | 0
Well Pump |  | 1500 | 0 | 750 | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
Total | 0 |  | 0 |  | 0 |  | 0

## Dedicated Loads Layout_EXAMPLE
|  |  | ILLUSTRATIVE EXAMPLE ONLY |  |  |  |  | Use this sheet when sizing one or more Pika Smart Batteries to provide backup power during outage events. Use the table to add loads, specifying the quantity, power, and duration requirements. The power specs of loads listed here are for general purposes. Check the specifications of the actual loads to be backed up. | Usable Energy | # Batteries
Sizing Dedicated Loads Panel for Backup Power | [7 empty] | Enter inputs in yellow cells only |  | 1 | 2 | 3 | 4
[8 empty] | Outputs appear in green cells | Harbor Plus | 17.1 | 34.2 | 51.3 | 68.4
Smart Battery Type | Harbor Plus | [7 empty] | Harbor Flex | 11.4 | 22.8 | 34.2 | 45.6
# of Smart Batteries | 1 | [7 empty] | Coral Smart Battery | 14 | 28 | 42 | 56
Max # of PV Links (for PV array) | 9 | [7 empty] | Continuous Power | # Batteries
[10 empty] | 1 | 2 | 3 | 4
| Units | Smart Battery Specs | Dedicated Loads System Requirements | Difference |  |  |  |  | Harbor Plus | 6.7 | 8 | 8 | 8
Max. Surge Power (up to 5 minutes) | W | 10000 | 7860 | 2140 |  |  |  |  | Harbor Flex | 4.5 | 8 | 8 | 8
Max. Continuous Power | W | 6700 | 5210 | 1490 |  |  |  |  | Coral Smart Battery | 8 | 8 | 8 | 8
Usable Energy Capacity | Wh | 17100 | 12620 | 4480
[9 empty] | Surge Power | # Batteries
Loads | Quantity | Surge Load (W) | Total Surge Load (W) | Continuous Load (W) | Total Continuous Load (W) | Duration (Hours) | Total Energy Required (Wh) |  |  | 1 | 2 | 3 | 4
Air Conditioner |  | 300 | 0 | 300 | 0 |  | 0 |  | Harbor Plus | 10 | 12 | 12 | 12
Boiler |  | 100 | 0 | 100 | 0 |  | 0 |  | Harbor Flex | 7 | 12 | 12 | 12
CFL Lightbulbs |  | 15 | 0 | 15 | 0 |  | 0 |  | Coral Smart Battery | 12 | 12 | 12 | 12
Chest Freezer |  | 200 | 0 | 200 | 0 |  | 0
Circulator Pumps | 1 | 600 | 600 | 150 | 150 | 6 | 900 |  | PV to Smart Battery Ratio | # Batteries
Electric Dryer |  | 3000 | 0 | 3000 | 0 |  | 0
Furnace Fan |  | 600 | 0 | 600 | 0 |  | 0 |  | # Batteries | 0 | 1 | 2 | 3 | 4
Heat Pump |  | 300 | 0 | 300 | 0 |  | 0 |  | Max PV Links | 12 | 9 | 6 | 3 | 0
LED Lightbulbs | 20 | 8 | 160 | 8 | 160 | 12 | 1920
Microwave |  | 900 | 0 | 900 | 0 |  | 0
Oven | 1 | 2400 | 2400 | 2400 | 2400 | 1 | 2400
Refrigerator | 1 | 200 | 200 | 200 | 200 | 12 | 2400
Resistive Heater | 1 | 1000 | 1000 | 1000 | 1000 | 2 | 2000
Small Appliances | 2 | 300 | 600 | 100 | 200 | 4 | 800
Stove |  | 1500 | 0 | 1500 | 0 |  | 0
Sump Pump | 1 | 1400 | 1400 | 350 | 350 | 2 | 700
TV |  | 300 | 0 | 300 | 0 |  | 0
Washing Machine |  | 800 | 0 | 800 | 0 |  | 0
Water Heater |  | 350 | 0 | 350 | 0 |  | 0
Well Pump | 1 | 1500 | 1500 | 750 | 750 | 2 | 1500
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
type other load here |  |  | 0 |  | 0 |  | 0
Total | 28 |  | 7860 |  | 5210 |  | 12620

## PV Link Sizing
|  |  | Use this sheet to determine the maximum and minimum number of solar panels that can be connected in series to a PV Link sub-string optimizer. Solar panels MUST be connected to PV Link in order to export power to a Pika inverter. |  |  | NEC Cold Factor | Min. Temp (C) | Min. Temp (F)
PV Link String Sizing |  |  | Enter inputs in yellow cells only |  |  | 1.02 | 24 to 20 | 76 to 68
|  |  | Outputs appear in green cells |  |  | 1.04 | 19 to 15 | 67 to 59
Site Specific Conditions | [5 empty] | 1.06 | 14 to 10 | 58 to 50
NEC Cold Temperature Factor | 1.18 |  |  |  |  | 1.08 | 9 to 5 | 49 to 41
Min. Temperature (C) | -11 to -15 | C |  |  |  | 1.1 | 4 to 0 | 40 to 32
Min. Temperature (F) | 13 to 5 | F |  |  |  | 1.12 | -1 to -5 | 31 to 21
|  |  | best for kyocera: 9 in series, 2 in parallel: 2844 WATT |  |  | 1.14 | -6 to -10 | 22 to 14
Solar Panel Specifications @ STC |  |  | Voc: 296 V temp corrected |  |  | 1.16 | -11 to -15 | 13 to 5
Total number of solar panels in array | 60 |  | Vmpp: 208.8 (9x23.2) |  |  | 1.18 | -16 to -20 | 4 to -4
PV array size |  | W |  |  |  | 1.2 | -21 to -25 | -5 to -13
Panel Manufacturer | kyocera |  |  |  |  | 1.21 | -26 to -30 | -14 to -22
Panel Model | 158G |  |  |  |  | 1.23 | -31 to -35 | -23 to -31
Rated Power (W) | 158 | W |  |  |  | 1.25 | -36 and below | -31 and below
Open Circuit Voltage (Voc) | 28.9 | V
Temperature corrected Voc | 34.102 | V
Max. Power Point Voltage (Vmp) | 23.2 | V
PV Link (S2501) Specifications
Max. Input Voltage (Voc) | 420 | V
MPPT Voltage Min. (Vmp) | 60 | V
MPPT Voltage Max. (Vmp) | 360 | V
Max. Current | 13 | A
| # PV modules in series | PV sub-array size (W)
Max. sub-array size per PV Link | 12 | 1896
Min. sub-array size per PV Link | 3 | 474 |  | quan | watt | total watt | volt | amp
|  |  |  | 80 | 158 | 12640 | 240 | 52.6667
Entire PV array:
Min. number of PV Links | 5
Min. number of wire runs to Pika inverter | 2
Additional Notes
1. Never mix and match panels: each discrete sub-string should be comprised of panels of the same make and model.
2. For high Voc modules (eg, Panasonic, SunPower), contact Pika for dual string input solutions.
3. For systems with three or more PV Links in parallel on the same wire run, check local codes for fusing requirements.

## PV Link Sizing_EXAMPLE
| ILLUSTRATIVE EXAMPLE ONLY |  | Use this sheet to determine the maximum and minimum number of solar panels that can be connected in series to a PV Link sub-string optimizer. Solar panels MUST be connected to PV Link in order to export power to a Pika inverter. | NEC Cold Factor | Min. Temp (C) | Min. Temp (F)
PV Link String Sizing |  |  | Enter inputs in yellow cells only | 1.02 | 24 to 20 | 76 to 68
|  |  | Outputs appear in green cells | 1.04 | 19 to 15 | 67 to 59
Site Specific Conditions |  |  |  | 1.06 | 14 to 10 | 58 to 50
NEC Cold Temperature Factor | 1.25 |  |  | 1.08 | 9 to 5 | 49 to 41
Min. Temperature (C) | -36 and below | C |  | 1.1 | 4 to 0 | 40 to 32
Min. Temperature (F) | -31 and below | F |  | 1.12 | -1 to -5 | 31 to 21
|  |  |  | 1.14 | -6 to -10 | 22 to 14
Solar Panel Specifications @ STC |  |  |  | 1.16 | -11 to -15 | 13 to 5
Total number of solar panels in array | 32 |  |  | 1.18 | -16 to -20 | 4 to -4
PV array size |  | W |  | 1.2 | -21 to -25 | -5 to -13
Panel Manufacturer | Q-Cells |  |  | 1.21 | -26 to -30 | -14 to -22
Panel Model | Q.Peak-G4 |  |  | 1.23 | -31 to -35 | -23 to -31
Rated Power (W) | 300 | W |  | 1.25 | -36 and below | -31 and below
Open Circuit Voltage (Voc) | 39.8 | V
Temperature corrected Voc | 49.75 | V
Max. Power Point Voltage (Vmp) | 32.4 | V
PV Link (S2501) Specifications
Max. Input Voltage (Voc) | 420 | V
MPPT Voltage Min. (Vmp) | 60 | V
MPPT Voltage Max. (Vmp) | 360 | V
Max. Current | 13 | A
| # PV modules in series | PV sub-array size (W)
Max. sub-array size per PV Link | 8 | 2400
Min. sub-array size per PV Link | 2 | 600
Entire PV array:
Min. number of PV Links | 4
Min. number of wire runs to Pika inverter | 2
Additional Notes
1. Never mix and match panels: each discrete sub-string should be comprised of panels of the same make and model.
2. For high Voc modules (eg, Panasonic, SunPower), contact Pika for dual string input solutions.
3. For systems with three or more PV Links in parallel on the same wire run, check local codes for fusing requirements.