## Sheet1
设备信息 |  | 配置参数
采集器SN | 3524160618 | Parameter Group | Parameter Item | Parameter Result | Last update time
Module Version No | LSW5BLE_17_840B_1.05 | Basic Settings | Work Mode | Self Consume | 2024-12-31 19:22:39 UTC -06:00
设备类型 | Inverter |  | PV input type | Independant
设备SN | F01237012089 |  | EPS/Backup Enable | Disable
Export Time | 2025-01-02 21:50:42 UTC -06:00 |  | Sell Enable | Disable
|  |  | CT Ratio | 1000
|  |  | Language | English
|  |  | Current time | 2024-12-31 07:40:19
|  |  | Week | Tuesday
|  | Basic Settings-2 | CT/Meter | CT | 2024-12-27 13:37:15 UTC -06:00
|  | OffGridWorkMode(Off-grid machine) | OffGridWorkMode | Bat Priority | 2024-12-31 09:34:05 UTC -06:00
|  | Battery Settings-Normal | Bat-Type | Lithium | 2024-12-30 10:01:01 UTC -06:00
|  |  | BMS Host | CAN
|  |  | Bat Charge Current | 100A
|  |  | Bat DisCharge Power Scale | 100%
|  | Battery Settings-Lithium | Bat On-Grid DOD | 50% | 2025-01-02 18:28:39 UTC -06:00
|  |  | Bat Off-Grid DOD | 50%
|  |  | OnGrid EodHyst | 15%
|  |  | OffGrid EodHyst | 20%
|  |  | Wake Up Enable | Enable
|  | Battery Settings-Lithium-2 | CAN_BMSID | 0 | 2024-12-30 10:01:32 UTC -06:00
|  | Battery Settings-Lead-Acid | Lead-acid Bat Capacity | 100AH | 2024-12-30 10:01:41 UTC -06:00
|  |  | Lead-acid Bat Float Volts | 55V
|  |  | Lead-acid Bat Max V | 58V
|  |  | Lead-acid Bat Min V | 43V
|  | Battery Settings-Lead-Acid-2 | Lead-acid Bat Absorption V | 56V | 2024-12-30 10:01:52 UTC -06:00
|  | Grid Settings-Normal | Grid Standard | US | 2024-12-30 10:01:59 UTC -06:00
|  |  | Grid Set | SplitPhase
|  |  | Grid Power Scale | 100%
|  | Grid Settings-Normal2 | American Standard Classification | UL1741&IEEE1547.2020 | 2024-12-30 10:02:08 UTC -06:00
|  | Grid Settings-Effective when Grid Standard selecting custom | Vac Min（Effective when Grid Standard selecting custom ） | 211V | 2024-12-30 10:02:14 UTC -06:00
|  |  | Vac Max（Effective when Grid Standard selecting custom ） | 264V
|  |  | Fac Min（Effective when Grid Standard selecting custom ） | 59.97Hz
|  |  | Fac Max（Effective when Grid Standard selecting custom ） | 60.03Hz
|  | Grid Settings-ConnectParameters | ReconnectFreqUp | 60.1Hz | 2025-01-02 07:47:22 UTC -06:00
|  |  | ReconnectFreqLow | 59.5Hz
|  |  | ReconnectVoltUp | 108%Un
|  |  | ReconnectVoltLow | 91.7%Un
|  |  | Inv NorRampRate | 0.33%Pn/S
|  |  | Inv SoftRampRate | 0.33%Pn/S
|  |  | grid reconnection time | 300.0S
|  | Grid Settings-VoltageProtect | Vac HV1 Trip | 110%/Vn | 2024-12-30 10:02:30 UTC -06:00
|  |  | Vac HV2 Trip | 120%/Vn
|  |  | Vac HV3 Trip | 120%/Vn
|  |  | Vac HV1 ClrTime | 2S
|  |  | Vac HV2 ClrTime | 0.16S
|  |  | VacHV3ClrTime | 0.16S
|  |  | Vac LV1 Trip | 88%/Vn
|  |  | Vac LV2 Trip | 70%/Vn
|  |  | Vac LV3 Trip | 45%/Vn
|  |  | Vac LV1 ClrTime | 20S
|  |  | Vac LV2 ClrTime | 5S
|  |  | Vac LV3 ClrTime | 0.32S
|  | Grid Settings-FrequencyProtect | Fac HF1 Trip | 61.2Hz | 2024-12-30 10:02:37 UTC -06:00
|  |  | Fac HF2 Trip | 62Hz
|  |  | Fac HF3 Trip | 62Hz
|  |  | Fac HF1 ClrTime | 300S
|  |  | Fac HF2 ClrTime | 0.16S
|  |  | Fac HF3 ClrTime | 0.16S
|  |  | Fac LF1 Trip | 58.5Hz
|  |  | Fac LF2 Trip | 56.5Hz
|  |  | Fac LF3 Trip | 56.5Hz
|  |  | Fac LF1 ClrTime | 300S
|  |  | Fac LF2 ClrTime | 0.16S
|  |  | Fac LF3 ClrTime | 0.16S
|  | Grid Settings-PU Curve | Generating Voltage Response | Disable | 2024-12-30 10:02:43 UTC -06:00
|  |  | Charging Voltage Response | Disable
|  |  | Vac Pwr Start | 106%/Vn
|  |  | Vac Pwr Stop | 110%/Vn
|  |  | Vac Pwr RspTime | 0.5S
|  | Grid Settings-PF Curve | Generating Frequency Response | Enable | 2024-12-30 10:02:57 UTC -06:00
|  |  | Charging Frequency Response | Enable
|  |  | Fac Pwr HFDb | 0.03Hz
|  |  | Fac Pwr HFK | 33%Pn/Hz
|  |  | Fac Pwr HFRspTime | 5S
|  |  | Fac Pwr LFDb | 0.03Hz
|  |  | Fac Pwr LFK | 33%Pn/Hz
|  |  | Fac Pwr LFRspTime | 0.5S
|  |  | Overfrequency recovery dead band | 0Hz
|  | Grid Settings-Reactive Type | Reactive Type | PowerFactor | 2024-12-30 10:03:03 UTC -06:00
|  |  | Power Factor | 1
|  |  | Reactive Power | 0
|  | Grid Settings-QU Curve | Vac VarV1 | 92% | 2024-12-30 10:03:10 UTC -06:00
|  |  | Vac VarV2 | 98%
|  |  | Vac VarV3 | 102%
|  |  | Vac VarV4 | 108%
|  |  | Vac VarQ1 | 44%
|  |  | Vac VarQ2 | 0%
|  |  | Vac VarQ3 | 0%
|  |  | Vac VarQ4 | 44%
|  |  | Var Var RspTime | 0.5S
|  |  | lockinPwr | 20%Pmax
|  |  | lockoutPwr | 5%Pmax
|  | Grid Settings-PQ Curve | PQ_P1 | N/A | N/A
|  |  | PQ_P2 | N/A
|  |  | PQ_P3 | N/A
|  |  | PQ_P1' | N/A
|  |  | PQ_P2' | N/A
|  |  | PQ_P3' | N/A
|  |  | PQ_Q1 | N/A
|  |  | PQ_Q2 | N/A
|  |  | PQ_Q3 | N/A
|  |  | PQ_Q1' | N/A
|  |  | PQ_Q2' | N/A
|  |  | PQ_Q3' | N/A
|  |  | PQ_response_time | N/A
|  | Grid Settings-cosφ(P) Curve (EU) | P/Pemax_a | 2% | 2024-12-30 07:59:23 UTC -06:00
|  |  | P/Pemax_b | 5%
|  |  | P/Pemax_c | 10%
|  |  | cosφ_a | 0
|  |  | cosφ_b | 0
|  |  | cosφ_c | -44
|  | Grid Settings-Voltage Ridethrough | LVRT enable | Enable | 2024-12-30 08:11:30 UTC -06:00
|  |  | HVRT enable | Enable
|  | Grid Settings-Detection Protection | Active Island Enable | Enable | 2024-12-30 09:04:53 UTC -06:00
|  |  | Leakage Current Detection Enable | Disable
|  |  | Insulation Detection Enable | Enable
|  | Others Settings | CT inversely | Disable | 2025-01-02 17:05:40 UTC -06:00
|  |  | Zero Export Power | 0
|  |  | home load enable | Enable
|  |  | no bat func | Disable
|  |  | BMS Aux manage | Disable
|  |  | BatLowCap Standby | Disable
|  |  | Forced OffGrid | Disable
|  |  | RSD Button En | Enable
|  |  | ARC Enable | Disable
|  |  | Ban Fast Check of Grid Voltage | Disable
|  |  | 10Min Over Volt | Disable
|  |  | Test Cmd2-Bit3 | Disable
|  |  | Test Cmd2-Bit5 | Enable
|  |  | Test Cmd2-Bit8 | Disable
|  |  | Test Cmd2-Bit9 | Disable
|  |  | Cancel Battery LV alarm | Disable
|  |  | DSP debug 485 | Disable
|  | Others Settings-2 | Grid Peak Shaving Enable | Disable | 2024-12-27 14:51:51 UTC -06:00
|  |  | Generator ramp Enable | Disable
|  |  | Test Cmd3-Bit2 | Disable
|  |  | Off Grid Display Abnormal | Disable
|  |  | Cei Eps Mutex | Disable
|  |  | Test Cmd3-Bit5 | Disable
|  |  | Test Cmd3-Bit6 | Disable
|  |  | Test Cmd3-Bit7 | Disable
|  |  | Test Cmd3-Bit8 | Disable
|  |  | Test Cmd3-Bit9 | Disable
|  |  | Test Cmd3-Bit10 | Disable
|  |  | Test Cmd3-Bit11 | Disable
|  |  | 208V 3Ph wiring check Prohibited | Disable
|  |  | L2 Reverse connection | Disable
|  |  | CT self check | Disable
|  | Peakshift | Charge start time1 | 10:00 | 2024-12-29 12:57:34 UTC -06:00
|  |  | Charge end time1 | 16:00
|  |  | Discharge start time1 | 00:00
|  |  | Discharge end time1 | 08:00
|  |  | Charge start time2 | 00:00
|  |  | Charge end time2 | 00:00
|  |  | Discharge start time2 | 00:00
|  |  | Discharge end time2 | 00:00
|  |  | Charge start time3 | 00:00
|  |  | Charge end time3 | 00:00
|  |  | Discharge start time3 | 00:00
|  |  | Discharge end time3 | 00:00
|  | Parallel Set | Parallel Enable | Disable | 2024-12-27 14:48:02 UTC -06:00
|  |  | Parallel Master/Slave | master
|  |  | Common Battery Enable | Disable
|  |  | Common GridCT Enable | Disable
|  |  | 3 Phase Enable | Disable
|  |  | Phase of this machine | A
|  |  | Parallel Num | 1
|  |  | Parallel Addr | 1
|  |  | Parallel Charge Current | 100A
|  |  | Parallel Discharge Current | 100A
|  | Generator Set | GEN Enable | Disable | 2024-12-28 11:48:06 UTC -06:00
|  |  | GEN Charge Enable | Disable
|  |  | GEN Auto Start | Disable
|  |  | GEN Manual On | Disable
|  |  | GEN Manual CMD | Disable
|  |  | GEN Connect to Grid Input | Disable
|  |  | GEN Start SOC（Lithium） | 20%
|  |  | GEN Stop SOC（Lithium） | 90%
|  |  | GEN Charges the Battery Current | 100A
|  |  | GEN Maximum Operating Time | 10hours
|  |  | GEN Cooling Time | 2hours
|  |  | GEN Power | 10000W
|  |  | GEN Stop2 SOC(Day Time)（Lithium） | 50%
|  |  | GEN Voltage Low | 200V
|  |  | GEN Voltage High | 260V
|  |  | GEN frequency Low | 45Hz
|  |  | GEN frequency High | 55Hz
|  |  | GEN Start Volt（Lead-acid） | 44V
|  |  | GEN Stop Volt（Lead-acid） | 54V
|  | Generator Set-2 | GEN WarmupTime | N/A | N/A
|  |  | GEN Stop PowerRatio | N/A
|  |  | Function Voltage Max Protection (average value at 10 minutes) | N/A
|  |  | GEN StopTime | N/A
|  | Advance Work Mode- Normal(L1,H1 and LNA model available) | Advance Work Mode | Disable | 2024-12-31 18:58:18 UTC -06:00
|  |  | Grid Charge Enable | Enable
|  |  | Bat Priority | Disable
|  |  | Charge Solar Only | Disable
|  |  | CT Limit Power | 0W
|  |  | Grid Capacity Power | 16000W
|  | Advance Work Mode- Normal(L1,H1 and LNA model available)-2 | AdvanMode Grid EodHyst | 5 | 2024-12-28 10:52:49 UTC -06:00
|  | Advance Work Mode- Normal(G2 and H3 model available) | Advance Work Mode (PV Energy Priority) | disable (load first) | 2024-12-31 18:59:04 UTC -06:00
|  |  | Grid Charge Enable | Enable
|  |  | Grid Consumption Limits Enable | Enable
|  |  | Constant Grid Power Enable | Enable
|  |  | Grid Power Limit Value | 0W
|  |  | Grid Capacity Power | 16000W
|  | Advance Work Mode -Time Slot | Time of Use Enable | Disable | 2025-01-01 09:19:41 UTC -06:00
|  |  | Slot1 Start Time | 00:00
|  |  | Slot1 Stop Time | 03:00
|  |  | Slot1 Power | 5000W
|  |  | Slot1 Bat Soc（Lithium） | 50%
|  |  | Slot1 Grid Charge Enable | Enable
|  |  | Slot1 Sell Enable | Disable
|  |  | Slot2 Start Time | 03:01
|  |  | Slot2 Stop Time | 07:00
|  |  | Slot2 Power | 5000W
|  |  | Slot2 Bat Soc（Lithium） | 50%
|  |  | Slot2 Grid Charge Enable | Enable
|  |  | Slot2 Sell Enable | Disable
|  |  | Slot3 Start Time | 07:01
|  |  | Slot3 Stop Time | 11:00
|  |  | Slot3 Power | 10000W
|  |  | Slot3 Bat Soc（Lithium） | 100%
|  |  | Slot3 Grid Charge Enable | Enable
|  |  | Slot3 Sell Enable | Disable
|  |  | Slot4 Start Time | 11:01
|  |  | Slot4 Stop Time | 15:00
|  |  | Slot4 Power | 10000W
|  |  | Slot4 Bat Soc（Lithium） | 50%
|  |  | Slot4 Grid Charge Enable | Disable
|  |  | Slot4 Sell Enable | Disable
|  |  | Slot5 Start Time | 15:00
|  |  | Slot5 Stop Time | 18:00
|  |  | Slot5 Power | 10000W
|  |  | Slot5 Bat Soc（Lithium） | 50%
|  |  | Slot5 Grid Charge Enable | Disable
|  |  | Slot5 Sell Enable | Disable
|  |  | Slot6 Start Time | 18:00
|  |  | Slot6 Stop Time | 23:59
|  |  | Slot6 Power | 10000W
|  |  | Slot6 Bat Soc（Lithium） | 50%
|  |  | Slot6 Grid Charge Enable | Disable
|  |  | Slot6 Sell Enable | Disable
|  | Advance Work Mode -Time Slot-2 | Slot1 Bat Volt（Lead-acid） | 44V | 2024-12-29 14:22:29 UTC -06:00
|  |  | Slot2 Bat Volt（Lead-acid） | 44V
|  |  | Slot3 Bat Volt（Lead-acid） | 44V
|  |  | Slot4 Bat Volt（Lead-acid） | 44V
|  |  | Slot5 Bat Volt（Lead-acid） | 44V
|  |  | Slot6 Bat Volt（Lead-acid） | 44V
|  | AC Couple | AC Couple ConnectTerminal | Disable | 2024-12-29 14:22:38 UTC -06:00
|  |  | AC Couple Trip SOC | 90%
|  |  | AC Couple Response Coefficient | 60
|  |  | AC Couple Trip Frequency | 65Hz
|  | Operational Modes（Custom） | Work Mode | Self Consume | 2025-01-01 09:20:50 UTC -06:00
|  |  | Grid Export Limit | 10000
|  |  | Export Options | Disable
|  | Battery Energy Management- Custom model available | Grid Support SOC | 10% | 2024-12-30 07:57:58 UTC -06:00
|  |  | Grid Chg End Soc | 100%
|  |  | Aux Load Soc On | 0%
|  |  | Aux Load Soc Off | 0%
|  |  | Restar Soc | 25%
|  |  | BatLowRecovereSOC | 10%
|  |  | BatLow Alarm SOC | 0%
|  |  | Discharge End SOC | 0%
|  |  | Aux Load Vol On | 44V
|  |  | Aux Load Vol Off | 40V
|  |  | Grid Support Volts | 44V
|  |  | Eod Hyst | 2V
|  | Battery 485 communication parameter- Custom model available | 485 Charge Voltage | 56.5V | 2024-12-30 07:57:42 UTC -06:00
|  |  | 485 Charge Voltage For Cur | 55.5V
|  |  | 485 Max Charge Current | 140A
|  |  | 485 Max DisCharge Current | 140A
|  |  | 485 BMS Version | 1
|  |  | 485 Cell Max ChargeVoltage | 3.65V
|  |  | 485 Cell Min ChargeVoltage | 2.65V
|  | Grid Settings-Custom model available | 10 minute OV protection threshold | 0V | 2024-12-31 09:53:04 UTC -06:00
|  |  | Function Voltage Max Protection (average value at 10 minutes) | 0S
|  |  | Initial start and restart after voltage interruption RED | 0S
|  |  | HVRT value | 0V
|  |  | LVRT value | 0V