## Disclaimer
SMA Sunny Boy TL-US with SPS - Quick Design Reference
Provided by SMA America, LLC
This tool is intended to be used in conjunction with: This tool is meant to be used in conjunction with:
SMA Sunny Boy TL-US with SPS inverters - SB 3000 / 3800 / 4000 / 5000 / 6000 / 7000 / 7700TL-US-22
DISCLAIMER
Use of this tool, or any information contained therein, by Any Parties shall constitute a waiver and release of SMA America, LLC from and against all claims and liability, including, but not limited to, claims for breach of contract, breach of warranty, strict liability, negligence, negligent misrepresentation, and/or otherwise, and liability for special, incidental, indirect, or consequential damages, in connection with such use. In addition, use of this tool, or any information contained therein by Any Parties, shall constitute agreement to defend and indemnify SMA America, LLC from and against any claims and liability, including, but not limited to, liability for special, incidental, indirect, or consequential damages in connection with such use. The benefit of such releases, waivers, or limitations of liability shall extend to, the related companies, and subcontractors of any tier of SMA America, LLC, and directors, officers, partners, employees, and agents of all released or indemnified parties.

## Instructions
SMA Sunny Boy TL-US with SPS - Quick Design Reference
INSTRUCTIONS
Overview
The SMA Sunny Boy TL-US with SPS - Quick Design Reference provides string design and inverter selection recommendations based on module specifications and design criteria specified by the user.
Module Description and Data
Enter the module description (manufacturer and model) and electrical specifications from the module datasheet. Module electrical data provided should be values for Standard Test Conditions (STC). Six electrical data values that are commonly provided on module manufacturer's datasheets are required:
- Maximum Power (Pmax) - may also be labeled Nominal Power, Peak Power, Rated Power, or similar
- Maximum Power Voltage (Vmp) - may also be labeled MPP Voltage, Voltage at Pmax, Rated Voltage, or similar
- Open Circuit Voltage (Voc)
- Maximum Power Current (Imp) - may also be labeled MPP Current, Current at Pmax, Rated Current, or similar
- Short Circuit Current (Isc)
- Temperature Coefficient of Voc (βvoc) - select the value from the drop-down selection list
Design Temperatures
Enter the design temperatures to be used in system design calculations.
Select °C or °F from the drop-down selection list to indicate whether design temperatures are specified in Celsius or Fahrenheit.
Minimum Low Temperature is used to calculate the maximum allowable string length that will not exceed the inverter's rated maximum system voltage. Typically an extreme low temperature is specified for this calculation to ensure the system remains below the rated maximum system voltage during all reasonably expected operating conditions.
Average High Temperature is used to calculate the recommended minimum string length to ensure the PV array maximum power voltage remains above the inverter's minimum operating voltage during warm operating conditions. Typically an average high summer temperature is specified for this calculation to ensure optimal energy harvest during warm summer operating temperatures.
(Note: A 30°C (86°F) cell temperature differential is added to the entered average high temperature in calculating recommended minimum string length. This cell temperature differential approximates cell operating temperatures in a typical residential rooftop installation.)
A hyperlink is provided to the Solar America Board for Codes and Standards (Solar ABCs) Solar Reference Map. This online tool can be used to look up reasonable design temperatures for a selected location.
Loading Ratio Preferences
Enter inverter loading preference thresholds for color-coding of inverter selection recommendations based on the PV array size.
Inverter loading ratio is the ratio of module array maximum power rating to the inverter nominal power rating (also known as DC:AC ratio). In a typical PV system the array will only infrequently achieve its maximum power rating, because actual real-world operating conditions are rarely equivalent to Standard Test Conditions (STC) at which module ratings are determined. For this reason it is customary to select an inverter with nominal power rating somewhat below the array maximum power rating.
Selecting an inverter based on inverter loading ratio is strictly a matter of balancing system costs with expected energy production. It is not possible to damage a Sunny Boy TL-US inverter by over-powering it. In a system designed with a high inverter loading ratio, the inverter may limit its output to its nominal power rating at times when the PV array would otherwise be capable of producing more power. The resulting power losses, known as clipping losses, may be relatively insignificant compared to the increased cost of an inverter with higher nominal output power - or the cost of an additional inverter. The amount of clipping losses will be determined by the inverter loading ratio in combination with system-specific design characteristics such as location, PV array tilt and orientation.
For most PV system designs an inverter loading ratio of 125% or lower will result in minimal, or possibly no, clipping losses. System designs with higher inverter loading ratios may make sense based on economic cost-benefit trade-offs or system-specific design characteristics. For example, a high inverter loading ratio may not result in significant clipping losses for a system design with multiple sub-arrays at different orientations, since the sub-arrays will not be expected to produce their maximum power at the same time of day.
AC Output Voltage
Select the AC output voltage for design recommendations - 240 VAC or 208 VAC.
Most residential installations will be 240 VAC. Sunny Boy TL-US inverters can also output 208 VAC for small commercial installations.
The nominal output power of some Sunny Boy TL-US models is determined by the AC output voltage. Inverter loading ratios are calculated based on the inverter nominal output power at the specified AC output voltage.
Printing
The Quick Design Reference has been formatted for printing on 8.5 x 11 inch paper. Print out your design recommendations and take them with you!

## SB TL-US-22 QDR
[15 empty] | Solar ABCs Temp Lookup | [9 empty] | Solar ABCs Temp Lookup
Module Description | [6 empty] | Module Data (STC) | [7 empty] | Design Temperatures |  |  |  |  | Loading Ratio Preferences |  |  |  |  | Wattage | 260
Sample Module 260W | [6 empty] | Maximum Power Voltage |  |  |  | Vmp | V | 30.7 |  | °C / °F |  |  | ⁰C |  | 85% | to | 99% | Min | 85% | Vmp | 30.7
Maximum Power |  |  | Pmax | W | 260 |  | Open Circuit Voltage |  |  |  | Voc | V | 37.9 |  | Minimum Low Temperature |  |  | -10 |  | 100% | to | 125% | Med | 125% | Voc | 37.9
[7 empty] | Maximum Power Current |  |  |  | Imp | A | 8.47 |  | Average High Temperature |  |  | 35 |  | 126% | to | 135% | Max | 135%
| Minimum String Length |  |  |  | 5 |  | Short Circuit Current |  |  |  | Isc | A | 9 | * | [10 empty] | Isc | 9
| Maximum String Length |  |  |  | 14 |  | Temperature Coefficient of Voc |  |  |  | βvoc | %/⁰C | -0.32% | [6 empty] | AC Output Voltage |  |  | VAC | 240 | Temp coeff | 0.32% | -0.32%
[5 empty] | * Module Isc exceeds allowable for 2 strings per input | [17 empty] | version 1.10
Total Modules | System Size (Wp DC) | Total Strings | [9 empty] | Nominal Output Power
|  | 1 | 2 |  | 3 |  |  | 4 |  |  |  | SB 3000TL-US |  | SB 3800TL-US |  | SB 4000TL-US | SB 5000TL-US |  | SB 6000TL-US |  | SB 7000TL-US |  | SB 7700TL-US |  | Low V | 125
|  | Modules per String - Input A / B | [9 empty] | 3000 |  | 3840 |  | 4000 | 5000 |  | 6000 |  | 7000 |  | 7680 |  | High V | 600
|  | A | A | B | A | A | B | A | A | B | B | Inverter Loading Ratio (DC:AC) | [12 empty] | Max ISC | 20
9 | 2340 | 9 | [9 empty] | 78% |  | 61% |  | 59% | 47% |  | 39% |  | 33% |  | 30% |  | 2 strings ISC | 18
[25 empty] | temperature difference | 35
0.112
[25 empty] | voltage rise at record low temperature | 4.2448
10 | 2600 | 10 | 5 | 5 | [7 empty] | 87% |  | 68% |  | 65% | 52% |  | 43% |  | 37% |  | 34% |  | Maximum Voltage per Module | 42.1448
[25 empty] | Maximum Modules per string | 14 | 14
[25 empty] | Temperature Coefficient of (VMP) | 0.0025921
[25 empty] | Minimum Voltage per Module | 25.5275
[25 empty] | Minimum Modules per string | 5 | 5
11 | 2860 | 11 | 5 | 6 | [7 empty] | 95% |  | 74% |  | 72% | 57% |  | 48% |  | 41% |  | 37%
[25 empty] | °C x 9/5 + 32 = °F | -10 |  | -23.3333
[25 empty] | (°F - 32) x 5/9 = °C | 35 |  | 1.6667
12 | 3120 | 12 | 5 | 7 | [7 empty] | 104% |  | 81% |  | 78% | 62% |  | 52% |  | 45% |  | 41%
|  |  | 6 | 6
13 | 3380 | 13 | 5 | 8 | [7 empty] | 113% |  | 88% |  | 85% | 68% |  | 56% |  | 48% |  | 44%
|  |  | 6 | 7
14 | 3640 | 14 | 5 | 9 | [7 empty] | 121% |  | 95% |  | 91% | 73% |  | 61% |  | 52% |  | 47%
|  |  | 6 | 8
|  |  | 7 | 7
15 | 3900 |  | 5 | 10 | 5 | 5 | 5 |  |  |  |  | 130% |  | 102% |  | 98% | 78% |  | 65% |  | 56% |  | 51%
|  |  | 6 | 9
|  |  | 7 | 8
16 | 4160 |  | 5 | 11 | 5 | 5 | 6 |  |  |  |  | 139% |  | 108% |  | 104% | 83% |  | 69% |  | 59% |  | 54%
|  |  | 6 | 10
|  |  | 7 | 9
|  |  | 8 | 8
17 | 4420 |  | 5 | 12 | 5 | 5 | 7 |  |  |  |  | 147% |  | 115% |  | 111% | 88% |  | 74% |  | 63% |  | 58%
|  |  | 6 | 11 | 6 | 6 | 5
|  |  | 7 | 10
|  |  | 8 | 9
18 | 4680 |  | 5 | 13 | 5 | 5 | 8 |  |  |  |  | 156% |  | 122% |  | 117% | 94% |  | 78% |  | 67% |  | 61%
|  |  | 6 | 12 | 6 | 6 | 6
|  |  | 7 | 11
|  |  | 8 | 10
|  |  | 9 | 9
19 | 4940 |  | 5 | 14 | 5 | 5 | 9 |  |  |  |  | 165% |  | 129% |  | 124% | 99% |  | 82% |  | 71% |  | 64%
|  |  | 6 | 13 | 6 | 6 | 7
|  |  | 7 | 12 | 7 | 7 | 5
|  |  | 8 | 11
|  |  | 9 | 10
20 | 5200 |  | 6 | 14 | 5 | 5 | 10 | 5 | 5 | 5 | 5 | 173% |  | 135% |  | 130% | 104% |  | 87% |  | 74% |  | 68%
|  |  | 7 | 13 | 6 | 6 | 8
|  |  | 8 | 12 | 7 | 7 | 6
|  |  | 9 | 11
|  |  | 10 | 10
21 | 5460 |  | 7 | 14 | 5 | 5 | 11 |  |  |  |  | 182% |  | 142% |  | 137% | 109% |  | 91% |  | 78% |  | 71%
|  |  | 8 | 13 | 6 | 6 | 9
|  |  | 9 | 12 | 7 | 7 | 7
|  |  | 10 | 11 | 8 | 8 | 5
22 | 5720 |  | 8 | 14 | 5 | 5 | 12 | 5 | 5 | 6 | 6 | 191% |  | 149% |  | 143% | 114% |  | 95% |  | 82% |  | 74%
|  |  | 9 | 13 | 6 | 6 | 10
|  |  | 10 | 12 | 7 | 7 | 8
|  |  | 11 | 11 | 8 | 8 | 6
23 | 5980 |  | 9 | 14 | 5 | 5 | 13 |  |  |  |  | 199% |  | 156% |  | 150% | 120% |  | 100% |  | 85% |  | 78%
|  |  | 10 | 13 | 6 | 6 | 11
|  |  | 11 | 12 | 7 | 7 | 9
[5 empty] | 8 | 8 | 7
[5 empty] | 9 | 9 | 5
24 | 6240 |  | 10 | 14 | 5 | 5 | 14 | 5 | 5 | 7 | 7 | 208% |  | 163% |  | 156% | 125% |  | 104% |  | 89% |  | 81%
|  |  | 11 | 13 | 6 | 6 | 12 | 6 | 6 | 6 | 6
|  |  | 12 | 12 | 7 | 7 | 10
[5 empty] | 8 | 8 | 8
[5 empty] | 9 | 9 | 6
25 | 6500 |  | 11 | 14 | 6 | 6 | 13 |  |  |  |  | 217% |  | 169% |  | 163% | 130% |  | 108% |  | 93% |  | 85%
|  |  | 12 | 13 | 7 | 7 | 11
[5 empty] | 8 | 8 | 9
[5 empty] | 9 | 9 | 7
[5 empty] | 10 | 10 | 5
26 | 6760 |  | 12 | 14 | 6 | 6 | 14 | 5 | 5 | 8 | 8 | 225% |  | 176% |  | 169% | 135% |  | 113% |  | 97% |  | 88%
|  |  | 13 | 13 | 7 | 7 | 12 | 6 | 6 | 7 | 7
[5 empty] | 8 | 8 | 10
[5 empty] | 9 | 9 | 8
[5 empty] | 10 | 10 | 6
27 | 7020 |  | 13 | 14 | 7 | 7 | 13 |  |  |  |  | 234% |  | 183% |  | 176% | 140% |  | 117% |  | 100% |  | 91%
[5 empty] | 8 | 8 | 11
[5 empty] | 9 | 9 | 9
[5 empty] | 10 | 10 | 7
[5 empty] | 11 | 11 | 5
28 | 7280 |  | 14 | 14 | 7 | 7 | 14 | 5 | 5 | 9 | 9 | 243% |  | 190% |  | 182% | 146% |  | 121% |  | 104% |  | 95%
[5 empty] | 8 | 8 | 12 | 6 | 6 | 8 | 8
[5 empty] | 9 | 9 | 10 | 7 | 7 | 7 | 7
[5 empty] | 10 | 10 | 8
[5 empty] | 11 | 11 | 6
29 | 7540 |  |  |  | 8 | 8 | 13 |  |  |  |  | 251% |  | 196% |  | 189% | 151% |  | 126% |  | 108% |  | 98%
[5 empty] | 9 | 9 | 11
[5 empty] | 10 | 10 | 9
[5 empty] | 11 | 11 | 7
[5 empty] | 12 | 12 | 5
30 | 7800 |  |  |  | 8 | 8 | 14 | 5 | 5 | 10 | 10 | 260% |  | 203% |  | 195% | 156% |  | 130% |  | 111% |  | 102%
[5 empty] | 9 | 9 | 12 | 6 | 6 | 9 | 9
[5 empty] | 10 | 10 | 10 | 7 | 7 | 8 | 8
[5 empty] | 11 | 11 | 8
[5 empty] | 12 | 12 | 6
31 | 8060 |  |  |  | 9 | 9 | 13 |  |  |  |  | 269% |  | 210% |  | 202% | 161% |  | 134% |  | 115% |  | 105%
[5 empty] | 10 | 10 | 11
[5 empty] | 11 | 11 | 9
[5 empty] | 12 | 12 | 7
[5 empty] | 13 | 13 | 5
32 | 8320 |  |  |  | 9 | 9 | 14 | 5 | 5 | 11 | 11 | 277% |  | 217% |  | 208% | 166% |  | 139% |  | 119% |  | 108%
[5 empty] | 10 | 10 | 12 | 6 | 6 | 10 | 10
[5 empty] | 11 | 11 | 10 | 7 | 7 | 9 | 9
[5 empty] | 12 | 12 | 8 | 8 | 8 | 8 | 8
[5 empty] | 13 | 13 | 6
33 | 8580 |  |  |  | 10 | 10 | 13 |  |  |  |  | 286% |  | 223% |  | 215% | 172% |  | 143% |  | 123% |  | 112%
[5 empty] | 11 | 11 | 11
[5 empty] | 12 | 12 | 9
[5 empty] | 13 | 13 | 7
[5 empty] | 14 | 14 | 5
34 | 8840 |  |  |  | 10 | 10 | 14 | 5 | 5 | 12 | 12 | 295% |  | 230% |  | 221% | 177% |  | 147% |  | 126% |  | 115%
[5 empty] | 11 | 11 | 12 | 6 | 6 | 11 | 11
[5 empty] | 12 | 12 | 10 | 7 | 7 | 10 | 10
[5 empty] | 13 | 13 | 8 | 8 | 8 | 9 | 9
[5 empty] | 14 | 14 | 6
35 | 9100 |  |  |  | 11 | 11 | 13 |  |  |  |  | 303% |  | 237% |  | 228% | 182% |  | 152% |  | 130% |  | 118%
[5 empty] | 12 | 12 | 11
[5 empty] | 13 | 13 | 9
[5 empty] | 14 | 14 | 7
36 | 9360 |  |  |  | 11 | 11 | 14 | 5 | 5 | 13 | 13 | 312% |  | 244% |  | 234% | 187% |  | 156% |  | 134% |  | 122%
[5 empty] | 12 | 12 | 12 | 6 | 6 | 12 | 12
[5 empty] | 13 | 13 | 10 | 7 | 7 | 11 | 11
[5 empty] | 14 | 14 | 8 | 8 | 8 | 10 | 10
[8 empty] | 9 | 9 | 9 | 9
37 | 9620 |  |  |  | 12 | 12 | 13 |  |  |  |  | 321% |  | 251% |  | 241% | 192% |  | 160% |  | 137% |  | 125%
[5 empty] | 13 | 13 | 11
[5 empty] | 14 | 14 | 9
38 | 9880 |  |  |  | 12 | 12 | 14 | 5 | 5 | 14 | 14 | 329% |  | 257% |  | 247% | 198% |  | 165% |  | 141% |  | 129%
[5 empty] | 13 | 13 | 12 | 6 | 6 | 13 | 13
[5 empty] | 14 | 14 | 10 | 7 | 7 | 12 | 12
[8 empty] | 8 | 8 | 11 | 11
[8 empty] | 9 | 9 | 10 | 10
39 | 10140 |  |  |  | 13 | 13 | 13 |  |  |  |  | 338% |  | 264% |  | 254% | 203% |  | 169% |  | 145% |  | 132%
[5 empty] | 14 | 14 | 11
40 | 10400 |  |  |  | 13 | 13 | 14 | 6 | 6 | 14 | 14 | 347% |  | 271% |  | 260% | 208% |  | 173% |  | 149% |  | 135%
[5 empty] | 14 | 14 | 12 | 7 | 7 | 13 | 13
[8 empty] | 8 | 8 | 12 | 12
[8 empty] | 9 | 9 | 11 | 11
[8 empty] | 10 | 10 | 10 | 10
41 | 10660 |  |  |  | 14 | 14 | 13 |  |  |  |  | 355% |  | 278% |  | 267% | 213% |  | 178% |  | 152% |  | 139%
42 | 10920 |  |  |  | 14 | 14 | 14 | 7 | 7 | 14 | 14 | 364% |  | 284% |  | 273% | 218% |  | 182% |  | 156% |  | 142%
[8 empty] | 8 | 8 | 13 | 13
[8 empty] | 9 | 9 | 12 | 12
[8 empty] | 10 | 10 | 11 | 11
44 | 11440 | [6 empty] | 8 | 8 | 14 | 14 | 381% |  | 298% |  | 286% | 229% |  | 191% |  | 163% |  | 149%
[8 empty] | 9 | 9 | 13 | 13
[8 empty] | 10 | 10 | 12 | 12
[8 empty] | 11 | 11 | 11 | 11
46 | 11960 | [6 empty] | 9 | 9 | 14 | 14 | 399% |  | 311% |  | 299% | 239% |  | 199% |  | 171% |  | 156%
[8 empty] | 10 | 10 | 13 | 13
[8 empty] | 11 | 11 | 12 | 12
48 | 12480 | [6 empty] | 10 | 10 | 14 | 14 | 416% |  | 325% |  | 312% | 250% |  | 208% |  | 178% |  | 163%
[8 empty] | 11 | 11 | 13 | 13
[8 empty] | 12 | 12 | 12 | 12
50 | 13000 | [6 empty] | 11 | 11 | 14 | 14 | 433% |  | 339% |  | 325% | 260% |  | 217% |  | 186% |  | 169%
[8 empty] | 12 | 12 | 13 | 13
52 | 13520 | [6 empty] | 12 | 12 | 14 | 14 | 451% |  | 352% |  | 338% | 270% |  | 225% |  | 193% |  | 176%
[8 empty] | 13 | 13 | 13 | 13
54 | 14040 | [6 empty] | 13 | 13 | 14 | 14 | 468% |  | 366% |  | 351% | 281% |  | 234% |  | 201% |  | 183%
56 | 14560 | [6 empty] | 14 | 14 | 14 | 14 | 485% |  | 379% |  | 364% | 291% |  | 243% |  | 208% |  | 190%
58 | 15080 | [10 empty] | 503% |  | 393% |  | 377% | 302% |  | 251% |  | 215% |  | 196%

## Data
INVERTER CUT SHEET INFORMATION
Inverter | Wattage | Low Voltage | High Voltage | Max ISC per channel
Select an Inverter
SB3000TLUS | 3000 | 125 | 600 | 19
SB3800TLUS | 3800 | 125 | 600 | 19
SB4000TLUS | 4000 | 125 | 600 | 19
SB5000TLUS | 5000 | 125 | 600 | 19
SB6000TLUS | 6000 | 125 | 600 | 19
SB7000TLUS | 7000 | 125 | 600 | 19
SB7700TLUS | 7700 | 125 | 600 | 19

## Calc
|  |  |  | SB 3000TL-US | SB 3800TL-US | SB 4000TL-US |  | SB 5000TL-US | SB 6000TL-US | SB 7000TL-US | SB 7700TL-US
|  |  | 240 | 3000 | 3840 | 4000 |  | 5000 | 6000 | 7000 | 7680
|  |  | 208 | 3000 | 3330 | 4000 |  | 4550 | 5200 | 6000 | 6650
[5 empty] | ⁰C | Low ⁰C | Low ⁰F
[5 empty] | ⁰F | -40 | -40
[6 empty] | -39 | -39
[6 empty] | -38 | -37
[6 empty] | -37 | -35
[6 empty] | -36 | -33
[6 empty] | -35 | -31
[6 empty] | -34 | -30
[6 empty] | -33 | -28
[6 empty] | -32 | -26
[6 empty] | -31 | -24
[6 empty] | -30 | -22
[6 empty] | -29 | -21
[6 empty] | -28 | -19
[6 empty] | -27 | -17
[6 empty] | -26 | -15
[6 empty] | -25 | -13
[6 empty] | -24 | -12
[6 empty] | -23 | -10
[6 empty] | -22 | -8
[6 empty] | -21 | -6
[6 empty] | -20 | -4
[6 empty] | -19 | -3
[6 empty] | -18 | -1
[6 empty] | -17 | 2
[6 empty] | -16 | 4
[6 empty] | -15 | 5
0% | -0.4% | 0.4% |  |  |  | -14 | 7
5% | -0.395% | 0.395% |  |  |  | -13 | 9
10% | -0.39% | 0.39% |  |  |  | -12 | 11
15% | -0.385% | 0.385% |  |  |  | -11 | 13
20% | -0.38% | 0.38% |  |  |  | -10 | 14
25% | -0.375% | 0.375% |  |  |  | -9 | 16
30% | -0.37% | 0.37% |  |  |  | -8 | 18
35% | -0.365% | 0.365% |  |  |  | -7 | 20
40% | -0.36% | 0.36% |  |  |  | -6 | 22
45% | -0.355% | 0.355% |  |  |  | -5 | 23
50% | -0.35% | 0.35% |  |  |  | -4 | 25
55% | -0.345% | 0.345% |  |  |  | -3 | 27
60% | -0.34% | 0.34% |  |  |  | -2 | 29
65% | -0.335% | 0.335% |  |  |  | -1 | 31
70% | -0.33% | 0.33% |  |  |  | 0 | 32
75% | -0.325% | 0.325% |  |  |  | 1 | 34
80% | -0.32% | 0.32% |  |  |  | 2 | 36
85% | -0.315% | 0.315% |  |  |  | 3 | 38
90% | -0.31% | 0.31% |  |  |  | 4 | 40
95% | -0.305% | 0.305% |  |  |  | 5 | 41
100% | -0.3% | 0.3% |  |  |  | 6 | 43
105% | -0.295% | 0.295% |  |  |  | 7 | 45
110% | -0.29% | 0.29% |  |  |  | 8 | 47
115% | -0.285% | 0.285% |  |  |  | 9 | 49
120% | -0.28% | 0.28% |  |  |  | 10 | 50
125% | -0.275% | 0.275% |  |  |  | 11 | 52
130% | -0.27% | 0.27% |  |  |  | 12 | 54
135% | -0.265% | 0.265% |  |  |  | 13 | 56
140% | -0.26% | 0.26% |  |  |  | 14 | 58
145% | -0.255% | 0.255% |  |  |  | 15 | 59
150% | -0.25% | 0.25% |  |  |  | 16 | 61
155% | [5 empty] | 17 | 63
160% | [5 empty] | 18 | 65
165% | [5 empty] | 19 | 67
170% | [5 empty] | 20 | 68
175%
180%
185%
190%
195%
200%